## 0.1 Version Control
NBN QA Checklist
NBN QA Checklist History
Current approved Version | NBN QA Checklist "L"
Person Responsible | Reason/Comment | Revision
John Hayes | First Draft _ Create sheets based on NBN Wireless Check list and QASIS | PA1
Don Farrow | Minor Format Changes | PA2
John Hayes | Combined SH and QASIS references | PA3
Troy Stephan | Approved | A
Dom Coomber | Re-submit to NBN as Draft | B
Dom Coomber | Added NBN Reference Documents | C
Dom Coomber | Included detailed references | D
Dom Coomber | Included NBN feedback and comment | E
Gene Martin | Updated & Amalgamated to include MS and FRS Learnings | F
Gene Martin | NBN Approved | G
Dom Coomber | Shelter Works Added | H
Doug Manning | Shelter Works Added | H+V2
Doug Manning | Shelter Works Added | J
Doug Manning | Minor adjustments to defect severity added | K
Doug Manning | Updated due to Document system issue with file name | L
Doug Manning | Updated based on field experience feedback | M

## 1.0 Header Information
Header Information
NBN Site Name | Young West | NBN Site Code | 2YON-51-07-YGWN
ASP Company | Visionstream
Auditor | Budiman Herwono | Audit Date | 2014-07-24
Auditor/Site Controller |  | Date
Instruction of Use
1. Build ASP to enter all Details in Header Information above (except Site Controller)
FOR CIVIL ACCEPTANCE
2. Build ASP to complete Tab 1.5 at MS4150 for MS4160 Civil Acceptance
3. Build ASP uploads Completed Checklist to SH (Acceptance/RAN Site Acceptance/MS5030/TDS4 QA Checklist)*
4. Build ASP emails Site Controller for Verification
5. Site Controller reviews & verifies complete.
FOR ICIO ACCEPTANCE
6. Build ASP to complete Tab 1.1 - 1.4 at MS5010 for MS5030 Installation & Commissioning Quality Acceptance
7. Build ASP uploads Completed Checklist to SH (Acceptance/RAN Site Acceptance/MS5030/TDS4 QA Checklist)
8. Build ASP emails Site Controller for Verification
9. Site Controller reviews & verifies complete.
10. Site Controller confirms complete to document controller for upload to SharePoint.
* Part Complete Checklist will loaded here until MS5030 reached.

## 1.1 Check List ODC & e-Node B
Site Name: |  | Young West | NBN Site Code: | 2YON-51-07-YGWN
Auditor: |  | Budiman Herwono | Audit Date: | 2014-07-24
ODC & e-Node B
N/A = Not applicable;
OK = Correctly installed;
Not OK = Not correctly installed, needs to be rectified;
NBN Ref | Item No. | General | Inspection Activity | Cat | OK |  | N/A | Comments
CAI-21 | 1 | The cabinet is clean and free from installation debris | Visual inspection. Removal of any foreign objects by hand. | Major
CAI-02 CAI-21 CAI-22 INS-05 | 2 | Cabinet damaged/scratched/rust | Visual inspection. Minor scratches allowed so long as base metal not exposed, touch up with paint. Minor impressions allowed so long as not impacting internal equipment. | Major
NBN Ref | Item No. | Rack/Cabinet Installation (SSC-02) | Inspection Activity | Cat | OK | Not OK | N/A | Comments
SSR-14 | 3 | The base frame & Cabinet positioned in accordance with the Site Construction Drawings | Check Redline mark-ups | Major
SSR-13 | 4 | Base frame anchored in accordance to the Site Construction Drawings | Confirm with FC Drawings. | Major
SSR-13 | 5 | Cabinet fastened to the base frame. Bolts torqued in accordance with manufacturers specifications | Check at least one bolt with calibrated torque wrench. (M8=18Nm / M12=80Nm). Ref. Doc. 2 1531-LZA 701 6009 (Installation of SSC02) | Major
INS-01 | 6 | Cabinet horizontally and vertically aligned | Use level to confirm. Up to +/- 3 degrees acceptable | Major
INS-03 | 7 | Ensure door free to open fully | Visual inspection. Door can fully open. | Major
INS-04 | 8 | Ensure all lifting eyes are removed from cabinets. Re-attached roof. | Visual inspection | Minor
INS-07 | 9 | Heat exchanger outlets not obstructed. | Visual inspection. Clear for 1m in front of exchanger | Major
INS-08 | 10 | All penetrations correctly sealed & water proofed | Visual inspection. Conduits sealed with PVC duct tape and cable entries using propriety glands. | Major
SIT-06 | 11 | Has the construction Barrel Lock been swapped to NBN Standard | Visual inspection. | Major
NBN Ref | Item No. | DC Power/Batteries | Inspection Activity | Cat | OK | Not OK | N/A | Comments
BBU-19 | 12 | Batteries in rack secured correctly, Installed as per Ref. Doc. 2 1531-LZA 701 6009 (Installation of SSC02) | Visual inspection | Critical
BBU-07 | 13 | DC Circuit Breakers installed as per the SID, Power Allocation Table | Battery CCB: 200A Climate CCB: 16A AMM 6P-1B: 16A AMM 6P-1A: 16A RRU CCBs: 25A - 32A | Critical
BBU-05 | 14 | DC cable installed correctly and colour coded (-48 Volts Blue / 0 Volt Red) | Visual inspection. Cables should be neat and tidy | Major
BBU-05 | 15 | DC-SPD internal cables installed correctly and colour coded with Blue (-48V) and Red (0V) heat shrink | Visual inspection. Cables should be neat and tidy | Major
BBU-19 | 16 | Batteries are installed to the installation manual & manufacturers specifications | Visual inspection. Refer to: NBN RAN installation MOP 1/198 17-3/FCP 121 6972 Installing Batteries 7/1531-LZA 701 6009 | Major
BBU-17 | 17 | Protection covers correctly installed on battery poles and Not damaged | Visual inspection. Refer to: NBN RAN installation MOP 1/198 17-3/FCP 121 6972 Installing Batteries 7/1531-LZA 701 6009 | Critical
BBU-06 | 18 | The gas evaporating tubes are correctly installed and routed out of cabinet via Gland in base plate. (length from batt 50mm) | Visual inspection. Refer to: NBN RAN installation MOP 1/198 17-3/FCP 121 6972 Installing Batteries 7/1531-LZA 701 6009 | Major
BBU-01 | 19 | Temperature sensor installed according to battery installation instructions | Visual inspection. Refer to: NBN RAN installation MOP 1/198 17-3/FCP 121 6972 Installing Batteries 7/1531-LZA 701 6009 | Major
BBU-9 | 20 | Spacers front and rear between batteries at correct height to ensure air flow | Visual inspection. Refer to: NBN RAN installation MOP 1/198 17-3/FCP 121 6972 Installing Batteries 7/1531-LZA 701 6009 | Major
BBU-16 | 21 | Batteries are labelled correctly | Check correct information on label as per NBN RAN Site Labelling Instruction 3/198 17-3/FCP 121 6972 | Major
CAI-10 | 22 | Power warning Labels fitted as per NBN RAN Site Labelling Instruction 3/198 17-3/FCP 121 6972 | Visual inspection | Major
NBN Ref | Item No. | Earthing | Inspection Activity | Cat | OK |  | N/A | Comments
CAI-19 | 23 | Cabinet earth cable is connected to the site SEB | Visual inspection. As per SID & NBN RAN installation MOP | Critical
BBU-11 | 24 | Earth grounding cable (Green/Yellow) has correct cross-section area as in SID and construction drawings | Visual inspection. As per SID & NBN RAN installation MOP | Major
BBU-11 | 25 | Base frame & SSC-02 earth cables labelled both ends | Visual inspection. Check label information is correct as per NBN RAN Site Labelling Instruction | Minor
BBU-15 | 26 | Cabinet earth grounded connection uses spring & flat washers and the nut tightened to torque of 18 Nm. | Visual inspection. Check Nut for Torque. Ref. Doc. 2 1531-LZA 701 6009 (Installation of SSC02) | Major
CAI-22 | 27 | TN and RBS earth cables to approach earth bolt 180° opposed | Visual inspection. NBN RAN installation MOP | Minor
EAT-08 | 28 | Earth grounding cable insulation undamaged | Visual inspection. Check for cable cuts. | Critical
RFF-20 | 29 | All earth lugs at SEB to be single hole type | Visual inspection. As per NBN RAN Mops 'NBN RAN Installation WI' | Critical
EAT-07 | 30 | Earth cable lugs crimped correctly. Heat shrink does not cover any of the flat contact area. | Visual inspection. As per NBN RAN Mops 'NBN RAN Installation WI' | Major
NBN Ref | Item No. | AC | Inspection Activity | Cat | OK |  | N/A | Comments
ACP-01 | 31 | AC feed installation quality and condition (fixing, protection) | Visual inspection. Cables are neat and tidy | Major
ACP-02 | 32 | Power Meter installed correctly and fully functional, supply ID label | Visual inspection Standard PDB/Metering Schematic. NBN-STD-0027 | Major
ACP-04 | 33 | Mud map from meter box to supply recorded in meterbox | Visual inspection | Major |  |  |  | Missing Mud Map
ACP-06 | 34 | Record check meter location & meter number | Recorded in SH (Civil works, Electrical) | Major
ACP-08 | 35 | Record generator input socket type & location on As-built drawings. | Standard PDB/Metering Schematic. NBN-STD-0027 | Major
ACP-11 | 36 | AC C/B installed to meter panel to be as per design. | Visual inspection - FC drawings. | Major
ACP-01 | 37 | Mains meter box power authority lock fitted | Visual inspection. Lock not broken | Major
ACP-02 | 38 | Mains meter box properly labelled | Visual inspection. Label has correct information as per Site Specific Signage | Minor
ACP-05 | 39 | Sub-mains box, built and installed to NBN standards. | Visual inspection. FC drawings & Design/Construction Specification. | Major
ACP-01 | 40 | Sub-mains box, is the Blue foam weather proofing present in bottom of meter box | Visual inspection. FC drawings & Design/Construction Specification. | Major
ACP-01 | 41 | Sub-mains box, is sub-board weatherproof | Visual inspection. FC drawings & Design/Construction Specification. | Major
NBN Ref | Item No. | RBS Main Unit Installation | Inspection Activity | Cat | OK |  | N/A | Comments
INS-01 INS-02 | 42 | Installed and positioned in accordance with the Site Installation Documentation (SID) | Confirm with SID the correct RU position. | Major
CAI-21 CAI-22 | 43 | Equipment undamaged and free from contamination | Visual inspection. Major dint or scratches not acceptable | Major
CAI-06 | 44 | The main unit is horizontally aligned | Use level to confirm. Check RU position is correct according to SID. | Major
CAI-06 | 45 | All cables in the front of the Main Unit are properly connected | Visual inspection. Cables should be neat and tidy | Major
CAI-07 | 46 | All screws are tightened to the correct torque | Check at least one screw with calibrated torque wrench. Refer to Doc. 3 1531-LZA 701 6009 (Installing RBS6601) | Major
CAI-06 | 47 | No cables are damaged | Visual inspection. Check for cuts in cables | Critical
CAI-08 | 48 | All cables are positioned as to enable the removal of cards/sub-racks without causing damage | Visual inspection. Cables should be neat and tidy | Major
APS-02 | 49 | Serial & Item numbers recorded as listed in the SID | Confirm with SID As-built | Major
NBN Ref | Item No. | Installation of Cables | Inspection Activity | Cat | OK |  | N/A | Comments
CAI-06 | 50 | All cables in the cabinet are correctly routed and connected | Visual inspection. Cables should be neat and tidy | Major
CAI-16 CAI-18 | 51 | All cable lugs crimped correctly. Heat shrink does not cover any of the flat contact area. | Visual inspection. As per NBN RAN Mops 'NBN RAN Installation MOP' | Major
CAI-06 | 52 | O/Fibre cables connected as per the SID Cable Table | Confirm with Site Installation Document | Critical
CAI-06 | 53 | Minimum bending radius of fibre optic cables complies with cable specifications | Visual inspection. As per manufacturers recommendation. | Major
CAI-06 | 54 | Optic cable installation & connection complies with the NBN RAN Installation MOP (1/198 17-3/FCP 121 6972 Uen) | Check cables run neatly, no sharp edges, secured correctly | Critical
| 55 | Alarm cables connection complies with the SID Alarm Allocation Table | Confirm with MOP and SID & Commissioning & Integration Checklist. Do visual inspection | Major
| 56 | GPS cable connection complies with SID Section 5.1 and 5.2 | Visual inspection. Confirm with SID | Major
CAI-14 | 57 | The MU DC power cable has been colour coded at circuit breaker connection | Red (0v) on grey cable Blue (-48v) on black | Major
CAI-06 | 58 | No cables or connectors are damaged | Visual inspection. Cables should be neat and tidy | Major
| 59 | Cable insulation to be butted to end of bootlace crimps | As per NBN MOPs. ' NBN RAN installation MOP' | Major
CAI-06 | 60 | All cables ties have been cut neatly with no sharp edges | Visual inspection. | Major
| 61 | Mains connected correctly to ODU Power Tray | Visual inspection. Cables rolled in ODU Power tray neatly. | Major
TOW-20 | 62 | Aircraft warning lights alarm and power cable labelled inside SSC02 (If applicable) | Visual inspection. As per Aircraft Warning Light Installation 29/198 17-3/FCP 121 6972. | Minor
| 63 | Ensure all CB and earth screws are tight | Visual inspection and physical move of cables to ensure none are loose | Critical
NBN Ref | Item No. | Installation of Roxtec Cable Entry Gland | Inspection Activity | Cat | OK |  | N/A | Comments
IES-13 IES-14 | 64 | Only one cable passes through each Roxtec module | Visual inspection. As per SSC02 installation manual | Major
CAI-04 | 65 | No centre cores are missing from unused Roxtec modules | Visual inspection. As per SSC02 installation manual | Major
IES-13 IES-14 | 66 | No visible gap between the cable and the module after compression | Visual inspection. As per SSC02 installation manual | Major
CAI-03 | 67 | The compression unit has been tightened as per Roxtec Inlet instruction manual attached. | Visual inspection. As per SSC02 installation manual | Major
CAI-03 | 68 | The Roxtec frame uses the supplied seal | Visual inspection. As per SSC02 installation manual | Critical
IES-14 | 69 | The cables are going straight through the frame (not bent in the module) | Visual inspection. As per SSC02 installation manual | Major
NBN Ref | Item No. | GPS install and earthing | Inspection Activity | Cat | OK |  | N/A | Comments
| 70 | GPS cables connected to GPS receiver in ICF have correct bend radii | Visual inspection. 'NBN RAN installation MOP' | Major
| 71 | GPS earthing connected to FEB at waterfall gantry | Visual inspection. 'NBN RAN installation MOP' | Major
| 72 | GPS installed correctly | Visual Inspection. 'NBN RAN installation MOP'/NBN STD.
NBN Ref | Item No. | Labelling | Inspection Activity | Cat | OK |  | N/A | Comments
MW-01 | 73 | The ACMA RAN Transmitter labels are fitted on the panel on the inside of the door | Visual inspection. Check ACMA information is correct as per SID and NBN RAN Site Labelling Instruction | Critical
ACP-02 BBU-03 | 74 | The Power Allocation label is fitted on the panel on the inside of the door | Visual inspection. Confirm with SID | Minor
| 75 | All fibre labels to be wrap type - no flag labels | Visual inspection, As per NBN RAN Site Labelling Instruction | Major
| 76 | All earth labels connected to SEB to be wrap type | Visual inspection, As per NBN RAN Site Labelling Instruction | Major
| 77 | Only Ericsson factory supplied internal cables (including sub-rack earths) to have flag type label - all others to be wrap around. Cables exiting ODU to have wrap label | Visual inspection, As per NBN RAN Site Labelling Instruction | Major
CAI-18 CAI-24 | 78 | All cables are labelled in accordance with NBN RAN Site Labeling (3/198 17-3/FCP 121 6972 Uen) | Check label positioning. Visual inspection | Minor
| 79 | ODF Fibre Tray labelled | Visual inspection, As per NBN RAN Site Labelling Instruction | Minor
CAI-24 | 80 | LTE Cat5 cable next to LMTB port labelled on DUS | Visual inspection. Check correct information | Minor
CAI-24 | 81 | LTE Fibre cables labelled for sector 1,2 & 3 at DUS | Visual inspection. Check proper labelling | Minor
Note on E8: Windows User: Ericsson Internal use
Note on E12: Windows User: Ericsson Internal use
Note on E23: Windows User: Ericsson Internal use
Note on E36: Windows User: Ericsson Internal use
Note on E46: Windows User: Ericsson Internal use
Note on E59: Windows User: Ericsson Internal use
Note on E69: Windows User: Ericsson Internal use
Note on E85: Windows User: Ericsson Internal use
Note on E93: Windows User: Ericsson Internal use
Note on E98: Windows User: Ericsson Internal use

## 1.2 Check List RRU & Antenna
Site Name: |  | Young West | NBN Site Code: | 2YON-51-07-YGWN
Auditor: |  | Budiman Herwono | Audit Date: | 2014-07-24
RRU & Antenna
N/A = Not applicable;
OK = Correctly installed;
Not OK = Not correctly installed, needs to be rectified;
NBN Ref | Item No. | RRU Installation | Inspection Activity | Cat | OK | Not OK | N/A | Comments
RFF-01 | 1 | RRU installed in location as specified in the FC Drawings | Visual inspection. Confirm with SID and site photographs. If possible use binoculars | Major
RFF-07 | 2 | An earth grounding cable is connected between the RRU and the earth bar connected to the SEB | Visual inspection. Confirm with site photographs. If possible use binoculars | Critical |  |  |  | RRU earthing need to rectify.
| 3 | Ground cable is connected to RRU with nut and washers and tightened to a torque of 15 Nm | Verify from pictures. As per MOP 'NBN RAN Installation MOP' | Major
| 4 | The earth grounding cable (Green/Yellow) has a minimum cross-section area of 35 mm² | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Major
| 5 | Protective covers, dust caps, and terminations plugs are installed on unused ports with Amalgamating tape around it | Verify from pictures. As per MOP 'NBN RAN Installation MOP' | Major
| 6 | Water proofing should be done using amalgamated tape and PVC on earth kits and connectors. | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Major
NBN Ref | Item No. | Antenna System Installation | Inspection Activity | Cat | OK | Not OK | N/A | Comments
RFF-01 | 7 | Antenna system installed as specified in the NBN RAN Installation MOP (1/198 17-3/FCP 121 6972) | Visual inspection. Confirm with SID & FC Drawing | Major
RFF-20 | 8 | Only one crimp lug connected to each ground bar or earth cleat connection point. Either one on back or one on front | Visual inspection. Confirm with site photographs. If possible use binoculars | Minor
RFF21 | 9 | All earth connections to use electrolytic paste. | Visual inspection. Confirm with site photographs. If possible use binoculars | Minor
RFF-22 | 10 | External feeder cables are to be labelled with stainless steel labels | Visual inspection. Check label information is correct as per NBN RAN Site Labelling Instruction | Major
RFF-15 | 11 | No cables or connectors are damaged | Visual inspection. Look for cable cuts and dents | Major
RFF-23 | 12 | Minimum bending radius of the RF jumper cables correct as specified in the manufacturer's specifications? | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Major
RFF-10 RFF-23 | 13 | RF jumper cables routed correctly and any excess cable neatly bundled and tied | Visual inspection. Confirm with site photographs. If possible use binoculars | Major
RFF-29 | 14 | RF jumper cables have bird protection fitted and are undamaged | Visual inspection. Confirm with site photographs. If possible use binoculars | Major
CAI-24 | 15 | Optical and DC cables are properly connected & labelled | Visual inspection. Check label information is correct as per NBN RAN Site Labelling Instruction | Minor
RFF-19 | 16 | Minimum bending radius of the optic cables correct as specified in to the manufacturer's specifications | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Major
RFF-25 | 17 | RRU Cable glands correctly assembled. If applicable | Visual inspection. Confirm with site photographs. If possible use binoculars | Major
RFF-29 | 18 | Horizontal cable runs fitted with specified Bird (parrot) penetration protection | Visual inspection.As per MOP 'NBN RAN Installation MOP' (Bird proofing should be all the way to he connector.) | Major
RFF-08 | 19 | Cable clamps spaced at a maximum of 1000mm on the vertical run | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Major
RFF-14 | 20 | Cable clamps or stainless steel cable ties spaced at a maximum of 800 millimetres on the horizontal run. | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Major
RFF-23 | 21 | Cables clamps secured correctly to the Cable ladder | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Major
SSR-17 | 22 | Bend or drip loop applied on cables (When Applicable) | Visual inspection. | Major
| 23 | H&S Cable sheath butted 20mm inside the SSC-02 cabinet cable gland and taped. | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Major
| 24 | Earth drain wire routed, lugged and connected to the SEB and heat shrink | Visual inspection. Check with SID on slot allocation | Critical
RFF-18 | 25 | Earth grounding kit installed in the cable gantry waterfall before entry into the cabinet base frame and connected to the FEB | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Critical
| 26 | Earth grounding kit installed 60cm before the lower bend connected to the lower earth bar. | Visual inspection.As per MOP 'NBN RAN Installation MOP'. Correct earth kits used for cable type. | Critical
| 27 | Connectors Water proofed with amalgamating tape and PVC | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Critical
| 28 | Antenna Spare ports Water proofed in accoradance with NBN RAN Installation MOP' | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Critical
| 29 | Water proofing ……(other) as per MOP 'NBN RAN Installation MOP' | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Critical
| 30 | Antenna Tilts are correct | Visual inspection. Antenna Tilts correspond with Redline Markups and SID document. | Critical
NBN Ref | Item No. | Installation of RRU Power Cables | Inspection Activity | Cat | OK | Not OK | N/A | Comments
| 31 | Power connector is securely and correctly attached using boot lace ferrules to RRU connector and DC-SPD | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Major
| 32 | DC power cables insulated in spaghetti tubing from the cable butt to the DC-SPD on the Interconnection Frame | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Major
| 33 | DC power cables do not restrict opening of the Interconnection Frame | Visual inspection. | Major
CAI-14 | 34 | DC power cables are colour code with Blue at the DC-SPD (-48V) and Red (0V) heat shrink | Visual inspection.As per MOP 'NBN RAN Installation MOP' | Major
CAI-20 | 35 | DC power cables are labelled | Visual inspection. Check label information is correct as per NBN RAN Site Labelling Instruction | Major
| 36 | RRU DC Power cables Earthing back to the Monopole cleat | Verify with pictures.As per MOP 'NBN RAN Installation MOP' | Major
| 37 | RRU DC Power cables earthing waterproofed with amalgamted tape and PVC. | Verify with pictures.As per MOP 'NBN RAN Installation MOP' | Major
Note on E8: Windows User: Ericsson Internal use
Note on E16: Windows User: Ericsson Internal use
Note on E42: Windows User: Ericsson Internal use

## 1.3 Check List Mini-Link TN
Site Name: |  | Young West | NBN Site Code: | 2YON-51-07-YGWN
Auditor: |  | Budiman Herwono | Audit Date: | 2014-07-24
Mini Link TN
N/A = Not applicable;
OK = Correctly installed;
Not OK = Not correctly installed, needs to be rectified;
NBN Ref | Item No. | Rack/Cabinet Installation (Indoor Cabin) | Inspection Activity | Cat | OK | Not OK | N/A | Comments
CAI-06 | 1 | Cabinet installed in accordance with the Site Installation Documentation (SID) and FC Drawings | Visual inspection. Confirm with SID. Differences captured in As-Built Drawing | Major
CAI-06 | 2 | Properly aligned and in level | Visual inspection.+/-3 degrees tolerance | Major
| 3 | Properly fastened to floor, wall or ladder | Visual inspection. Refer to Cabinet Installation Manual | Major
CAI-20 | 4 | Internal cables properly installed | Visual inspection. Cables should be neat and tidy | Major
CAI-13 | 5 | DC cable properly installed; rack/cabinet supplied with power | Visual inspection. Check label information is correct as per NBN RAN Site Labelling Instruction | Critical
BBU-07 | 6 | Circuit Breaker installed and not tripped | Visual inspection. Check correct CB rating and SID allocation | Major
BBU-15 | 7 | Rack/cabinet ground connected to site SEB | Visual inspection. Refer to 'NBN RAN Installation MOP' | Critical
SPB-01 | 8 | General Configuration Data sheet properly filled in | Check Configuration Data sheet in SID | Critical
NBN Ref | Item No. | AMM and Other Units | Inspection Activity | Cat | OK | Not OK | N/A | Comments
CAI-06 | 9 | AMM, fan unit and all other units fitted in the rack/cabinet in accordance with the SID | Visual inspection. Confirm with SID cabinet allocation section. | Critical
CAI-06 | 10 | Plug-in units in correct positions and properly connected to the front of the AMM | Visual inspection. Confirm with SID cabinet allocation section. | Critical
CAI-07 | 11 | Plug-in units properly tightened | Visual inspection. Refer to Minilink TN Installation Manual and RAN Installation MOP | Critical
CAI-06 | 12 | Dummy panels installed | Visual inspection. Refer to Minilink TN Installation Manual and RAN Installation MOP | Major
CAI-06 | 13 | AMM, fan unit and optional units correctly grounded | Visual inspection. Refer to Minilink TN Installation Manual and RAN Installation MOP | Major
NBN Ref | Item No. | Connectors and Cables | Inspection Activity | Cat | OK | Not OK | N/A | Comments
CAI-08 | 14 | Traffic cables properly installed | Visual inspection. Check label information is correct as per NBN RAN Site Labelling Instruction | Major
MW-06 | 15 | Radio cable correctly assembled and tightened to the radio unit | Visual inspection. Refer to Minilink TN Installation Manual and RAN Installation MOP | Major
RFF-25 | 16 | Radio cable correctly sealed with butyl and at least two layers of PVC tape at MW Radio Cable and 7.6mm Feeder splice(Near MMU side) | Visual inspection. Refer to 'NBN RAN Installation MOP' | Major
CAI-19 | 17 | Radio cable grounding (earthing) kit correctly installed and tightened | Visual inspection. Refer to 'NBN RAN Installation MOP' | Major
MW-02 | 18 | A & B DC power feeds identfied at AMM | Visual inspection. Refer to PFU3B board on AMM | Minor
ODF-02 | 19 | Patch leads (CAT5/6 & Fibre) of the specified type & routed correctly (No hand made patch cables allowed) | Visual inspection. Refer to SID and NBN RAN Installation MOP | Major
MW-03 | 20 | All cards and SFP’s etc are secured, active and not in alarm. | Visual inspection. | Critical
MW-06 | 21 | Minilink MMU to RAU coax(s) installed, N- connector tightened, supported. | Visual inspection. Refer to 'NBN RAN Installation MOP' | Major
RFF-17 RFF-18 | 22 | Radio cable grounded to FEB in the waterfall assembly before entrering cabinet | Visual inspection. Refer to 'NBN RAN Installation MOP' | Major
NBN Ref | Item No. | General | Inspection Activity | Cat | OK | Not OK | N/A | Comments
MW-01 | 23 | ACMA Transmitter Labels attached to each Radio Cable at the MMU connection | Visual inspection. Check label information is correct as per NBN RAN Site Labelling Instruction | Critical
Note on E8: Windows User: Ericsson Internal use
Note on E18: Windows User: Ericsson Internal use
Note on E25: Windows User: Ericsson Internal use
Note on E36: Windows User: Ericsson Internal use

## 1.4 Check List MW Antenna
Site Name: |  | Young West | NBN Site Code: | 2YON-51-07-YGWN
Auditor: |  | Budiman Herwono | Audit Date: | 2014-07-24
MW Antenna
N/A = Not applicable;
OK = Correctly installed;
| Not OK = Not correctly installed, needs to be rectified; |  |  | Cat = QASIS
NBN Ref | Item No. | Antenna and Outdoor Accessories | Inspection Activity | Cat | OK | Not OK | N/A | Comments
TOW-04 | 1 | Antenna located in accordance with the FC Drawings. | Visual inspection. Confirm with FC Drawings | Critical
TOW-08 | 2 | Microwave Antenna - Is the "Property of NBN Co." label on back Dish(one on top and one on bottom) | Visual inspection. Use Binoculars to check bottom sticker and Site Photos. | Critical
TOW-20 | 3 | Aircraft warning lights installed as per design (if applicable) | Visual inspection using binoculars to check. Confirm with FC Drawings | Critical
TOW-01 | 4 | Antenna structure - Ladder support bracket fitted | Visual inspection using binoculars to check. Confirm with FC Drawings | Major
TOW-03 | 5 | Antenna structure - is Ladsafe installed | Visual inspection using binoculars to check. Confirm with FC Drawings | Major
HSE-18 | 6 | Antenna structure - is Ladsafe tagged | Visual inspection using binoculars to check. Confirm with FC Drawings | Major
NBN Ref | Item No. | Radio Cable | Inspection Activity | Cat | OK | Not OK | N/A | Comments
RFF-13 RFF-14 | 7 | Radio cable fastened with the recommended distance between clamps | Visual inspection. Vertical Run: 1m apart, Horizontal run 0.8m apart | Major
RFF-16 RFF-17 | 8 | Radio cable grounding installed where the cable runs straight only | Visual inspection. Refer to Minilink TN Installation Manual and RAN Installation MOP | Major
TOW-30 | 9 | Radio cable grounded to FEB or cleats in the mast and before entering the building | Visual inspection. Refer to Minilink TN Installation Manual and RAN Installation MOP | Major
IES-13 IES-14 | 10 | Radio cable correctly inserted through the cable lead-in (ROXTEC) | Visual inspection. Refer to Minilink TN Installation Manual and RAN Installation MOP | Major
RFF-19 | 11 | Bending of the radio cable does not exceed minimum bending radius | Visual inspection. Installing Outdoor Equip MiniLink.pdf Sect 10.2 Table 4 | Major
RFF-11 | 12 | Radio cable sheath not damaged | Visual inspection for cable cuts. | Critical
TOW-28 | 13 | Radio cable labelled | Visual inspection. Check label information is correct as per NBN RAN Site Labelling Instruction | Major
Note on E8: Windows User: Ericsson Internal use
Note on E16: Windows User: Ericsson Internal use

## 1.5 Check List Civils
Site Name: |  | Young West | NBN Site Code: | 2YON-51-07-YGWN
Auditor: |  | Budiman Herwono | Audit Date: | 2014-07-24
Construction
N/A = Not applicable;
OK = Correctly installed;
Not OK = Not correctly installed, needs to be rectified;
NBN Ref | Item No. | General Document Verification | Inspection Activity | Cat | OK | Not OK | N/A | Comments
| 1 | Site Access Document | Accuracy of submitted artefacts verified. | Critical
| 2 | As Built Drawing | Accuracy of submitted artefacts verified. | Major
| 3 | Fibre scoping | Accuracy of submitted artefacts verified. | Critical
| 4 | IF/GPS cable testing | Accuracy of submitted artefacts verified. | Critical
NBN Ref | Item No. | General Site | Inspection Activity | Cat | OK | Not OK | N/A | Comments
| 5 | General Layout | Visual inspection, confirmation compound layout as per As Built Drawings & NBN Co STD drawings/design specifications. | Critical
| 6 | Compound/Rooftop(As applicable) | Ground levelling and slope is according to NBN Co STD drawings/design specifications. | Major
| 7 | Fencing / Gates | Visual inspection, confirmation with As Built Drawings & NBN Co STD drawings/design specifications. No damage and straight | Critical
| 8 | Compound Weed Mat and Gravel | Weed matting and minimum 100mm 20mm nominal gravel spread across compound. No weeds or plants growing in compound. | Minor
| 9 | Civil & Cabinet Foundations | Visual inspection confirming neat finishing of tower/cabinet foundations. Edges clean and straight and to FC drawing size. | Major
| 10 | Cabinet Plinth/s | Cabinet support frame installed as per NBN Co STD drawings and located as per FC drawings. Max 5mm gap between cover and foundation. | Major
| 11 | Ducts | Visual Inspection confirming ducts are installed as per FC drawings / Redlines and sealed with PVC tape. Unused ducts to have draw rope. | Minor
| 12 | Gantry Installation | Visual inspection with As Built Drawings & NBN Co STD drawings. Gantry supported & connected to cabinet plinth and tower. | Critical
| 13 | Gantry Support Poles | Visual inspection. Gantry support as per redlines and foundation as per design guide. No movement at foundation and connected to the tower. Galvanising complete and no rust. | Critical
| 14 | New Tower / Monopole Structure | Visual Inspections confirming structure is as per FC / redlines and visibly vertical. Galvanising is complete and no rust present. | Minor
| 15 | New Tower Headframe | Headframe correctly orientated as per FC drawings / updated redlines | Critical
| 16 | Antenna Mount Locations for NBN Antennas | Antenna mounts correctly orientated as per the FC drawings / Redline Mark-ups, galvanised and no rust present | Critical
| 17 | Antenna Mount Drainage for NBN mounts | Drain holes on all Circular Hollow Section mounts | Major
| 18 | Climbing Ladder for New GF sites | Climbing ladder is installed according to assembly instructions and visually vertical | Critical
| 19 | Tower Grouting for new GF sites | Grouting below base plates is complete with drainage. 20mm straight PVC conduit (not flexible conduit) | Major
| 20 | Structure Earthing | Structure is connected to earth ring. | Critical
| 21 | Fencing / Gate Earthing | Fencing and Gates earthed correctly to NBN Co STD drawings/design specifications. | Major
| 22 | DC & AC Earthing | Visible check DC &AC earth connection to earth bars/pits as per design | Major
| 23 | MET Earthing | MET is connected to the ground system | Critical
| 24 | Earth Bars | Earth bars for feeder grounding installed as per NBN Co STD drawings/design specifications | Critical
| 25 | Gantry Earthing | Outdoor Gantry/Cable ladders are grounded correctly | Critical
| 26 | Compound Earthing | Installed as per FC drawings and Redlines. All connections tight. | Critical
| 27 | AC Earthing | AC mains power box is connected to earth. As per electrical design pertinent to site and in accordance to AS3000. | Critical
| 28 | Electrical Distribution Cabinet | Visual inspection confirming electrical cabinet is installed as per FC drawings and located on H Frame (where required) | Major
| 29 | Site Access i.e. Tracks/Culverts | Access is as per Design guide and redline drawings. Water drainage is according to design specification. | Critical
| 30 | Site Clean and Tidy | Garbage and surplus construction materials cleared from site. No foreign items that can be picked up. | Major
| 31 | Construction Quality | Visual inspection, confirmation with As Built Drawings & NBN Co STD drawings/design specifications. | Critical
| 32 | Signage | Compliance with NBN Co design hand book, Standard Drawings and approved design (As Built) | Major
| 33 | EME Compliance | Visual inspection, confirmation with As Built Drawings & NBN Co STD drawings/design specifications. | Critical
| 34 | Feeder / IF cable Type | Confirm feeder type installed matches SID and redlines | Major
| 35 | Any cuts, holes & welds to existing steelwork shall be treated with "cold galv" zinc rich paint. | Visual inspection. As per NBN Standard Construction Notes (NBN-STD-0001) – “Structural Steelwork” Note 7. | Minor
| 36 | Gantry window cable protection on monopoles | Visual inspection. Cable protection is required at the gantry windows. | Minor
| 37 | Cable Ties | Correct cable ties used. In accordance with NBN Specification/STD. | Minor
Note on E8: Windows User: Ericsson Internal use
Note on E14: Windows User: Ericsson Internal use

## 1.6 Check List Shelter & eNodeB
Site Name: |  | Young West | NBN Site Code: | 2YON-51-07-YGWN
Auditor: |  | Budiman Herwono | Audit Date: | 2014-07-24
Shelter & e-Node B
Superfelous = Not applicable;
OK = Correctly installed;
Not OK = Not correctly installed, needs to be rectified;
NBN Ref | Item No. | General | Inspection Activity | Cat | OK | NotOK | N/A | Comments
CAI-21 | 1 | The cabinet/shelter is clean and free from installation debris | Visual inspection. Removal of any foreign obects by hand. Note: Protective floor covers can be left on floor until ALL contruction/ audit activities are completed | Major
CAI-02 CAI-21 CAI-22 INS-05 | 2 | Cabinet/Shelter damaged/scratched/rust | Visual inspection. Minor scratches allowed so long as base metal not exposed, touch up with paint. Minor impressions allowed so long as not impacting internal equipment. | Major
NBN Ref | Item No. | Shelter Installation - General | Inspection Activity | Cat | OK | NotOK | N/A | Comments
| 3 | The Shelter positioned in accordance with the Site Construction Drawings | Check Redline markups | Major
| 4 | Shelter anchored in accordance to the Site Construction Drawings | Confirm with FC Drawings. | Major
| 5 | Cabinets horizontally and vertically aligned | Visual Inspection for verticality | Major
| 6 | Cabinet spacing in accordance with the SID | Confirm with FC Drawings. | Minor
| 7 | Ensure door free to open fully | Visual inspection. Door can fully open. | Minor
| 8 | All penetrations correctly sealed & water proofed | Visual inspection. Conduits sealed with PVC duct tape and cable entries using propriety glands. | Major
| 9 | Has the construction Barrel Lock been swapped to NBN Standard for Shelter door and compound | Visual inspection. | Major
NBN Ref | Item No. | Shelter Installation - Environmental | Inspection Activity | Cat | OK | NotOK | N/A | Comments
| 10 | Air Conditioner | Physical inspection - ensure air conditioner is working after shelter install and settings are correct. Note: Ensure Air conditioners are in the on position | Critical
| 11 | DC FAN - FX1800B | DC powered forced ventilation of the facility shall be activated in case of AC power outage for cooling purposes- Tested and working. | Critical
| 12 | Lighting | Internal Florescent (DC) emergency light working. | Major
| 13 |  | Exterior light above entry door working. | Major
NBN Ref | Item No. | Shelter Installation - Physical Security | Inspection Activity | Cat | OK | NotOK | N/A | Comments
| 14 | Door locking | Standard mechanical lock with secure key-tested | Major
| 15 |  | Door provided with an internal emergency release - tested | Minor
NBN Ref | Item No. | Shelter Installation - Fire Protection, Detection & Control | Inspection Activity | Cat | OK | Not OK | N/A | Comments
| 16 | Fire extinguisher | Visual Inspection - ensure fire extinguisher is secure and in the correct position and an up to date inspection tag is attached or marked on the cylinder . | Major
| 17 | Illuminated emergency exit sign | Illuminated emergency exit sign installed | Major
NBN Ref | Item No. | DC Power/Batteries | Inspection Activity | Cat | OK | Not OK | N/A | Comments
BBU-19 | 18 | Batteries in rack secured correctly, Installed as per Ref. Doc. 21/1531-LZA 701 6009 | Visual inspection: Refer to: NBN RAN installation MOP 1/198 17-3/FCP 121 6972 Installing Batteries 7/1531-LZA 701 6009 | Critical
BBU-07 | 19 | DC Circuit Breakers installed as per the SID, Power Allocation Table with respective alarm sense wires connected to each breaker | Battery CCB: 200A Climate CCB: 16A AMM 6P: 16A AMM 20P: 40A AMM 20P FAU: 6A RRU CCBs: 25A - 32A | Critical
BBU-05 | 20 | DC cable installed correctly and colour coded (-48 Volts Blue / 0 Volt Red) | Visual inspection. Cables should be neat and tidy | Major
BBU-17 | 21 | Protection covers correctly installed on battery poles and Not damaged | Visual inspection. Refer to: NBN RAN installation MOP 1/198 17-3/FCP 121 6972 Installing Batteries 7/1531-LZA 701 6009 PBC6200 Installation: 21/1531-LZA 701 6009 | Critical
BBU-01 | 22 | Temperature sensor installed according to battery installation instructions | Visual inspection. Refer to: NBN RAN installation MOP 1/198 17-3/FCP 121 6972 Installing Batteries 7/1531-LZA 701 6009 PBC6200 Installation: 21/1531-LZA 701 6009 | Major
BBU-9 | 23 | Spacers front and rear between batteries at correct height to ensure air flow | Visual inspection. Refer to: NBN RAN installation MOP 1/198 17-3/FCP 121 6972 Installing Batteries 7/1531-LZA 701 6009 PBC6200 Installation: 21/1531-LZA 701 6009 | Major
BBU-16 | 24 | Batteries are labelled correctly | Visual inspection. Refer to: NBN RAN installation MOP 1/198 17-3/FCP 121 6972 | Major
CAI-10 | 25 | Power warning Labels fitted as per NBN Shelter Installation WI 43/198 17-3/FCP 121 6972 | Visual inspection | Major
| 26 | No unprotected cables or connections protruding from PBC6200 | Visual Inspection | Critical
NBN Ref | Item No. | Earthing | Inspection Activity | Cat | OK | Not OK | N/A | Comments
CAI-19 | 27 | Shelter earth cable is connected to the site SEB | Visual inspection. As per SID & NBN RAN installation MOP | Critical
BBU-11 | 28 | Earth grounding cable (Green/Yellow) has correct cross-section area as in SID and construction drawings | Visual inspection. As per SID & NBN RAN installation MOP | Major
BBU-11 | 29 | Base frame earth cables labelled both ends | Visual inspection. Check label information is correct as per NBN RAN Site Labelling Instruction | Minor
BBU-15 | 30 | Shelter earth grounded connection uses spring & flat washers and the nut tightened to torque of 18 Nm. | Visual inspection. Check Nut for Torque. Ref. Doc. 2 1531-LZA 701 6009 (Installation of SSC02) | Major
CAI-22 | 31 | Equipment earth cables secured to rack earth bars and Rack earth cables connected to MET | Visual inspection. NBN Shelter Installation WI Also confirm as per SID | Minor
EAT-08 | 32 | Earth grounding cable insulation undamaged | Visual inspection. Check for cable cuts. | Critical
RFF-20 | 33 | All earth lugs at SEB to be single hole type | Visual inspection. As per NBN RAN Mops 'NBN RAN Installation WI' | Critical
EAT-07 | 34 | Earth cable lugs crimped correctly. Heat shrink does not cover any of the flat contact area. | Visual inspection. As per NBN RAN Mops 'NBN RAN Installation WI' | Major
NBN Ref | Item No. | AC | Inspection Activity | Cat | OK | Not OK | N/A | Comments
ACP-01 | 35 | AC feed installation quality and condition (fixing, protection) | Visual inspection. Cables are neat and tidy Note: To the best of the auditors ability if he is not an electrician | Major
ACP-02 | 36 | Power Meter installed correctly and fully functional, supply ID label | Visual inspection Standard PDB/Metering Schematic. NBN-STD-0027 Note: To the best of the auditors ability if he is not an electrician | Major
ACP-04 | 37 | Mud map from meter box to supply recorded in meter box | Visual inspection | Major
ACP-06 | 38 | Record check meter location & meter number | Recorded in SH (Civilworks, Electrical) | Major
ACP-08 | 39 | Record generator input socket type & location on As-built drawings. | Standard PDB/Metering Schematic. NBN-STD-0027 | Major
ACP-11 | 40 | AC C/B installed to meter panel to be as per design. | Visual inspection - FC drawings. | Major
ACP-01 | 41 | Mains meter box power authority lock fitted | Visual inspection. Lock not broken | Major
ACP-02 | 42 | Mains meter box properly labelled | Visual inspection. Label has correct information as per Site Specific Signage | Minor
ACP-05 | 43 | Sub-mains box, built and installed to power industry standards | Visual inspection. FC drawings & Design/Construction Specification. | Major
NBN Ref | Item No. | RBS Main Unit Installation | Inspection Activity | Cat | OK | Not OK | N/A | Comments
INS-01 INS-02 | 44 | Installed and positioned in accordance with the Site Installation Documentation (SID) | Confirm with SID the correct RU position. | Major
CAI-21 CAI-22 | 45 | Equipment undamaged and free from contamination | Visual inspection. Major dint or scratches not acceptable | Major
CAI-06 | 46 | The main unit is horizontally aligned | Use level to confirm. Check RU position is correct according to SID. | Major
CAI-06 | 47 | All cables in the front of the Main Unit are properly connected | Visual inspection. Cables should be neat and tidy | Major
CAI-07 | 48 | All screws are tightened to the correct torque | Check at least one screw with calibrated torque wrench. Refer to Doc. 3 1531-LZA 701 6009 (Installing RBS6601) | Major
CAI-06 | 49 | No cables are damaged | Visual inspection. Check for cuts in cables | Critical
CAI-08 | 50 | All cables are positioned as to enable the removal of cards/subracks without causing damage | Visual inspection. Cables should be neat and tidy | Major
APS-02 | 51 | Serial & Item numbers recorded as listed in the SID | Confirm with SID As-built | Major
NBN Ref | Item No. | Installation of Cables | Inspection Activity | Cat | OK | Not OK | N/A | Comments
CAI-06 | 52 | All cables in the cabinet are correctly routed and connected | Visual inspection. Cables should be neat and tidy and are not to run across any sharp edges | Major
CAI-06 | 53 | All Optic Fibre cables connected as per the SID Cable Table | Confirm with Site Installation Document | Critical
CAI-06 | 54 | Minimum bending radius of fibre optic cables complies with cable specifications | Visual inspection. As per manufacturers recommendation. | Major
CAI-06 | 55 | Optic cable installation & connection complies with the NBN RAN Installation MOP (1/198 17-3/FCP 121 6972 Uen) | Check cables run neatly, no sharp edges, secured correctly | Critical
| 56 | Alarm cables connection complies with the SID Alarm Allocation Table | Confirm with MOP and SID & Commissioning & Integration Checklist. Do visual inspection | Major
| 57 | GPS cable connection complies with SID Section 5.1 and 5.2 | Visual inspection. Confirm with SID | Major
CAI-14 | 58 | The MU DC power cable has been colour coded at circuit breaker connection | Red (0v) on grey cable Blue (-48v) on black | Major
CAI-06 | 59 | No cables or connectors are damaged | Visual inspection. Cables should be neat and tidy | Major
| 60 | Cable insulation to be butted to end of bootlace crimps | As per NBN MOPs. ' NBN RAN installation MOP' | Major
CAI-06 | 61 | All cables ties have been cut neatly with no sharp edges | Visual inspection. | Major
TOW-20 | 62 | Aircraft warning lights alarm and power cable labelled inside shelter (If applicable) | Visual inspection. As per Aircraft Warning Light Installation 29/198 17-3/FCP 121 6972. | Minor
| 63 | Optical Fibre Patch Leads | Required - Suggest changing to " Optical patch leads meet CTO-376 and inspection report is available on demand | Major
| 64 | Optic Fibre Spur Cabling Refer to: NBN-CNI-CWP-018 | Shelter Hub sites will have an NBN fibre tail installed to an OEF in the middle of the AMM20P Tx rack. The fibre could be either ribbon or standard style and consist of 12 fibres. These fibres will exit/enter the shelter via a vertical cable ladder leading to the factory fitted conduit below the primary gland window. Once installed the conduit will be sealed against water and vermin. | Major
NBN Ref | Item No. | Shelter Installation - Feeder Entry Gland Plate | Inspection Activity | Cat | OK | NotOK | N/A | Comments
| 65 | Feeder Entry | Visual inspection - ensure feeder entries are adequately bird proofed / protected by the cable tray covers. | Major
| 66 |  | Visual inspection - ensure feeders entering through gland plate are installed neatly and compression glands adequately tightened. | Major
| 67 |  | Visual inspection - ensure feeders entering through gland plate meet bending requirements and have acceptable drip bends to prevent water ingress through the glands. | Major
IES-13 IES-14 | 68 | Only one cable passes through each Roxtec module | Visual inspection. | Major
CAI-04 | 69 | No centre cores are missing from unused Roxtec modules | Visual inspection. | Major
IES-13 IES-14 | 70 | No visible gap between the cable and the module after compression | Visual inspection. | Major
CAI-03 | 71 | The compression unit has been tightened as per Roxtec Inlet instruction manual attached. | Visual inspection. | Major
IES-14 | 72 | The cables are going straight through the frame (not bent in the module) | Visual inspection. | Major
NBN Ref | Item No. | GPS install and earthing | Inspection Activity | Cat | OK | Not OK | N/A | Comments
| 73 | GPS cables connected to GPS receiver below entry gland and has correct bend radii | Visual inspection. 'NBN RAN installation MOP' | Major
| 74 | GPS earthing connected to FEB at feeder entry window | Visual inspection. 'NBN RAN installation MOP' | Major
| 75 | GPS installed correctly | Visual Inspection. 'NBN RAN installation MOP'/NBN STD. | Major
NBN Ref | Item No. | Labelling | Inspection Activity | Cat | OK | Not OK | N/A | Comments
MW-01 | 76 | The ACMA RAN Transmitter labels are fitted to the side of the rack near the eNodeB | Visual inspection. Check ACMA information is correct as per SID and NBN RAN Site Labelling Instruction. (as per CNI-008) | Critical
ACP-02 BBU-03 | 77 | The Power Allocation labels are fitted to both the SPD and PBC6200 doors | Visual inspection. Confirm with SID | Minor
| 78 | All fibre labels to be wrap type - no flag labels | Visual inspection, As per NBN RAN Site Labelling Instruction(as per CNI-008) | Major
| 79 | All earth labels connected to SEB to be wrap type | Visual inspection, As per NBN RAN Site Labelling Instruction | Major
| 80 | Only Ericsson factory supplied internal cables (including subrack earths) to have flag type label - all others to be wrap around. | Visual inspection, As per NBN RAN Site Labelling Instruction(as per CNI-008) | Major
CAI-18 CAI-24 | 81 | All cables are labelled in accordance with NBN RAN Site Labeling (3/198 17-3/FCP 121 6972 Uen) | Check label positioning. Visual inspection | Major
| 82 | ODF Fibre Tray labelled | Visual inspection, As per NBN RAN Site Labelling Instruction | Major
CAI-24 | 83 | LTE Cat5 cable next to LMTB port labelled on DUS | Visual inspection. Check correct information | Major
CAI-24 | 84 | LTE Fibre cables labelled for sector 1,2 & 3 at DUS | Visual inspection. Check proper labelling | Major
| 85 | NBN specific shelter signage applied to Door | Visual inspection | Major
| 86 | Fibre Spur cable labelled as per NBN specs | Visual inspection. Refer to NBN RAN Labelling and NBN-CNI-CWP-008 for details | Major
Note on E8: Windows User: Ericsson Internal use
Note on E11: Windows User: Ericsson Internal use
Note on E19: Windows User: Ericsson Internal use
Note on E24: Windows User: Ericsson Internal use
Note on E27: Windows User: Ericsson Internal use
Note on E30: Windows User: Ericsson Internal use
Note on E40: Windows User: Ericsson Internal use
Note on E49: Windows User: Ericsson Internal use
Note on E59: Windows User: Ericsson Internal use
Note on E68: Windows User: Ericsson Internal use
Note on E82: Windows User: Ericsson Internal use
Note on E91: Windows User: Ericsson Internal use
Note on E95: Windows User: Ericsson Internal use